# Smart Street Light Feeder Panel + CMS

Project Report: design, wiring, parts list, build aur testing

Rev B · 10 October 2026

Table of Contents

# 1. Project overview

| Item | Detail |
| --- | --- |
| Project | CMS: Central Monitoring System for street lights (tender) |
| Scope | 160 smart feeder panels, ~40,000 poles (~250 poles per panel) |
| Panel | 3-phase, 10 kW, 4G/LTE, energy meter data on CMS dashboard |
| Prepared for | RAHUL |
| Repository | github.com/roxjaglan000-ui/cms (PR #1 panel, PR #2 CMS software) |
| Status | Design complete. Firmware not yet compiled or tested on hardware. |

Ye report tender ke 3-phase, 10 kW Smart Feeder Control Panel ka poora design hai. Panel street lights ko time ya sunset/sunrise ke hisaab se ON-OFF karta hai, 3-phase energy meter padhta hai, faults pakadta hai, aur 4G se CMS dashboard ko data bhejta hai. Dashboard se panel ko turant command bhi de sakte hain.

Is report se aap ye kaam kar sakte ho:

- Parts kharidna (Section 6)

- Panel banana aur wiring karna (Sections 3–5, 9)

- Firmware daalna aur CMS jodna (Sections 7–8)

- Har panel ki testing aur site commissioning (Section 10)

- Tender bid ka hisaab (Section 11)

## 1.1 Tender requirements

Tender spec (screenshot)

| # | Requirement (from spec) | Covered in |
| --- | --- | --- |
| 1 | SITC of 3-phase, 10 kW smart feeder control panel for street lights, with incomer, outgoing and 5-year comprehensive warranty | Sections 2–6 |
| a | Panel communicates with the application over 4G/LTE/5G, with no delay in response | 4G modem + persistent MQTT connection, commands applied immediately (Section 7) |
| b | Compartmentalised aluminium busbar with full neutral, MCB incomer and outgoing | Section 3 |
| b1 | Scheduling by time of day, day of week/month, date | ASTRO, SCHEDULE (weekday mask) and special-date modes (Section 7) |
| b2 | Alarming and flexible reporting | ThingsBoard alarm rules and reports (Section 8) |
| b3 | Data logging with historical data repositories | Telemetry every 5 min (configurable) plus instant events, offline buffer in flash, history in ThingsBoard |
| b4 | Failure detection and reporting | Fault table in Section 7 |
| b5 | Event and fault logging | event telemetry key, RAISED/CLEARED per fault |
| c | 3-phase energy meter data shown on the CMS dashboard | Selec MFM383A-C (or SDM630) over Modbus RS485 |
| — | 12 m hot-dip galvanised octagonal poles on existing pedestals | Civil/supply item, outside this design |
| — | 6 mm laminated sheet inside the pole window box | Civil/supply item |
| — | 63 A terminal block for 16/25 sq mm conductor, 4 nos, on DIN channel | Per pole, Section 6.2 |
| — | 6 A SP MCB C-curve, 2 nos, earth stud, per pole | Per pole, Section 6.2 |

# 2. System design

Block diagram

Kaise kaam karta hai: supply incomer, SPD aur energy meter se hoke aluminium busbar pe aati hai. Wahan se contactor K1 aur RCCB ke through do outgoing feeders tak jaati hai. Controller (ESP32 + 4G) har 5 second meter padhta hai, decide karta hai light ON ho ya OFF, relay se contactor chalata hai, MCB aur door jaise inputs check karta hai, aur MQTT se CMS ko data bhejta hai.

## 2.1 Load calculation (10 kW panel)

I = P ÷ (√3 × V × PF) = 10,000 ÷ (1.732 × 415 × 0.95) ≈ 14.6 A per phase. LED drivers ka inrush zyada hota hai, isliye incomer aur contactor 40 A rakhe hain.

| Item | Value |
| --- | --- |
| Supply | 415 V, 3-phase + N |
| Poles per panel | 40,000 ÷ 160 = 250 (≈ 83 per phase) |
| Max lamp jo 10 kW me fit hoga | 10,000 W ÷ 250 = ≈ 40 W per pole |
| Current per phase | ≈ 14.6 A |

Sabse zaroori check: 10 kW panel me 250 pole tabhi chalenge jab har lamp lagbhag 40 W ka ho. Lamp 60–90 W ke hain to panel 15–22.5 kW ka banana padega (neeche table). Tender BOQ me lamp ki watt zaroor dekho.

## 2.2 Panel rating by lamp wattage (250 poles)

| Lamp | Load | Current / phase | Incomer | RCCB 300 mA | Contactor | CTs | Feeder MCBs (×6) | iMax | Extra cost vs 10 kW |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 40 W | 10 kW | 14.6 A | 4P MCB 40 A | 4P 40 A | 4P 40 A AC-1 | 30/5 | 16 A | 25 | — |
| 60 W | 15 kW | 22 A | 4P MCB 63 A | 4P 63 A | 4P 63 A AC-1 | 50/5 | 20 A | 35 | ₹3,000–4,500 |
| 90 W | 22.5 kW | 33 A | 4P MCB 63 A (or 80 A MCCB) | 4P 63 A | 4P 63 A AC-1 | 50/5 | 25 A | 50 | ₹4,000–6,000 |

Meter, controller, enclosure aur firmware same rehte hain. Sirf CMS se setLimits aur meter ka CT ratio setting badalna hai.

# 3. Power wiring

Power wiring (main circuit)

Raasta: Supply → 4P MCB 40 A incomer → SPD (earth tak) → Selec MFM383A-C energy meter (3 CT, R/Y/B pe) → aluminium busbar → contactor K1 → 4P RCCB 40 A 300 mA → 2 outgoing feeders (A aur B), har feeder me 3 SP MCB 16 A aur 4-core cable.

Control supply R-bus aur N se do 6 A MCB ke through li jaati hai (SMPS aur contactor coil ke liye).

Har 6 outgoing MCB ke baad ek 230 V opto channel hai. Ye controller ko batata hai kaun sa MCB trip hua. Agar 6 ke 6 ek saath band hon to RCCB trip hua hai.

Colour code (Indian): R lal, Y peela, B neela, Neutral kaala, Earth hara. Power wiring 6 sq mm Cu (terminal blocks pe spec ke hisaab se 16/25 sq mm), control wiring 1.5 sq mm Cu, signal wiring 0.5–0.75 sq mm.

## 3.1 Feeder design for 250 poles

- 2 three-phase feeder, 3 single-phase nahi. Sadak ki har direction me ek 4-core cable, aur pole pe lamp R, Y, B, R, Y, B… baari baari jodo. Phase balance rehta hai aur voltage drop single-phase ke mukable lagbhag 6 guna kam.

- RCCB 300 mA. 2–3 km lambe feeder ke end pe phase-earth fault itna current nahi kheenchta ki 16 A MCB trip ho. RCCB earth fault kahin bhi ho, trip karega. CEA safety regulations bhi 5 kW se upar earth leakage protection maangte hain.

- Har pole me 6 A MCB (spec me hai) us pole ka lamp circuit bachata hai, taaki ek lamp ki kharabi sirf usi pole ko band kare.

## 3.2 Feeder cable aur voltage drop

Example: har feeder pe 125 pole, 2.5 km sadak, R-Y-B balanced, aluminium armoured 4-core cable. Far end pe drop ≈ I × R × L ÷ 2.

| Lamp | Current / phase / feeder | 16 sq mm Al | 25 sq mm Al | 35 sq mm Al | 50 sq mm Al |
| --- | --- | --- | --- | --- | --- |
| 40 W | 7.6 A | 7.9% | 5.0% | 3.6% | — |
| 60 W | 11.4 A | — | 7.4% | 5.4% | 4.0% |
| 90 W | 17.1 A | — | — | 8.1% | 6.0% |

Lagbhag 5% tak rakho. Asli route length site survey se lekar dobara nikaalo. Panel apne area ke beech me rakho, taaki dono taraf ke feeder chhote rahein.

# 4. Control wiring

Control wiring (contactor coil)

Selector switch ke 3 position hain:

- AUTO: contactor coil relay RL1 se chalti hai, jo controller (GPIO23) chalata hai.

- OFF: lights band.

- MANUAL: coil seedhe supply se. Controller kharab ho tab bhi lights jala sakte ho.

Contactor ka aux NO contact ek 230 V opto channel pe jaata hai, taaki controller ko pata chale contactor sach me band hua.

# 5. Controller wiring (low voltage)

Controller wiring

| ESP32 pin | Connected to | Note |
| --- | --- | --- |
| GPIO18 / GPIO19 | TTL-RS485 module TXD / RXD → meter A, B | Auto-direction module, twisted pair, 120 Ω at the end |
| GPIO21 / GPIO22 | DS3231 RTC SDA / SCL | Keeps time without network |
| GPIO23 | Relay module IN → RL1 | Opto-isolated relay |
| GPIO35 | Door limit switch | LOW = door closed, 10k pull-up |
| GPIO36 | Contactor aux NO via 230 V opto | LOW = contactor on, 10k pull-up |
| GPIO21 / GPIO22 (I2C) | PCF8574 expander at 0x20, P0–P5 ← opto after MCBs A-R, A-Y, A-B, B-R, B-Y, B-B | LOW = supply present |
| GPIO15 | Selector AUTO position (extra contact block) | LOW = AUTO |
| 5V / GND | 230 V → 5 V 3 A SMPS | The 4G modem draws up to 2 A peaks |
| SIM / antenna | Nano SIM, 4G antenna mounted outside the panel | Metal enclosures block signal |

GPIO 34–39 sirf input hain aur inme internal pull-up nahi hota: GPIO35 aur GPIO36 pe 10 kΩ pull-up (3.3 V tak) lagao. Pin numbers LilyGO T-A7670E ke hisaab se hain; board aane pe uska pinout ek baar mila lo. 4G antenna panel ke bahar lagao, metal panel signal rokta hai.

# 6. Parts list (ek panel, 10 kW)

Rates October 2026 ke andaaze hain. Brand, shehar aur quantity ke hisaab se 15–25% upar-neeche ho sakte hain. Bid se pehle vendor quote zaroor lo.

| # | Item | Spec / example | Qty | Approx ₹ |
| --- | --- | --- | --- | --- |
| 1 | Panel enclosure | CRCA 16/14 SWG, IP55, powder coated, ~500×400×200 mm, compartmentalised, from a local fabricator | 1 | 5,000–6,500 |
| 2 | Incomer | 4P MCB 40 A C-curve (the spec asks for an MCB incomer) | 1 | 1,600–2,200 |
| 3 | Surge protection device | Type 2, 3P+N, 20 kA. Not in the spec; keep it to protect the 5-year warranty | 1 | 1,500–2,000 |
| 4 | Aluminium busbar set | R, Y, B, N strips + SMC insulators | 1 | 1,200–1,800 |
| 5 | 3-phase energy meter | Selec MFM383A-C (RS485) + 3 CT 30/5 A. Indian make | 1 | 3,800–4,400 |
| 6 | Power contactor | 4P 40 A AC-1, 230 V coil, + 1NO aux, reputed Indian brand | 1 | 1,800–2,500 |
| 7 | Outgoing MCB | SP 16 A C-curve, 3 per feeder × 2 feeders | 6 | 900–1,200 |
| 7a | RCCB (earth leakage) | 4P 40 A, 300 mA. Required by CEA safety regulations for loads above 5 kW; also protects the long feeders | 1 | 2,000–2,800 |
| 8 | Control MCB | SP 6 A C-curve | 2 | 300 |
| 9 | Selector switch | 3-position AUTO-OFF-MAN, 22 mm | 1 | 200–250 |
| 10 | Indicator lamps | 22 mm LED: R, Y, B, Light ON | 4 | 240–300 |
| 11 | Controller + 4G | LilyGO T-A7670E (ESP32 + A7670 LTE Cat-1) with antenna | 1 | 2,300–2,800 |
| 12 | Power supply | 230 V AC → 5 V 3 A SMPS (replaces 12 V SMPS + buck) | 1 | 350–500 |
| 13 | Backup cell | 18650 Li-ion (fits the board’s holder) | 1 | 200–250 |
| 14 | RTC module | DS3231 | 1 | 120–150 |
| 15 | RS485 module | TTL ↔ RS485, auto direction | 1 | 100–150 |
| 16 | Relay module | 1-channel 5 V opto-isolated | 1 | 80–120 |
| 17 | AC sense module | 230 V opto-isolated, 8 channel (6 outgoing MCBs + contactor aux + spare) | 1 | 400–500 |
| 17a | I/O expander | PCF8574 I2C module (reads the 6 MCB inputs) | 1 | 80–120 |
| 18 | Door limit switch |  | 1 | 100–150 |
| 19 | Antenna extension | SMA cable + panel-mount antenna | 1 | 250–300 |
| 20 | Terminal blocks | 63 A for 16/25 sq mm × 4 (spec), control terminals | 1 set | 900–1,100 |
| 21 | Wiring material | Cu wire, lugs, ferrules, DIN rail, duct, glands | 1 set | 1,500–2,000 |
| 22 | Earthing | Earth bar, stud, washers | 1 set | 250–300 |
|  | Panel total (excluding poles, lights, cable, labour) |  |  | ≈ 25,500–32,500 |

In parts me kanjoosi mat karna: spec me 5 saal ki comprehensive warranty hai. Contactor, MCB, RCCB, SMPS, earthing aur IP55 enclosure achhe brand ke lo. Yahan ₹500 bachaoge to baad me ₹5,000 site visit me lagenge.

## 6.1 Prototype ke liye extra (ek baar)

| Item | Qty | Approx ₹ |
| --- | --- | --- |
| USB-C data cable (flashing ke liye) | 1 | 200 |
| RS485 → USB adapter (meter ko PC se check karne ke liye) | 1 | 250 |
| Digital multimeter, clamp meter | 1 each | 2,500–4,000 |
| 500 V insulation tester (megger), earth tester, RCD tester | rent / electrician se | — |
| Test load: 6–10 LED lamps ya heater (bench test) | 1 set | 2,000–3,000 |

## 6.2 Har pole ka saamaan (spec ke hisaab se)

| Item (per pole) | Approx ₹ |
| --- | --- |
| 63 A terminal block (16/25 sq mm), 4 nos, DIN channel pe | 400–600 |
| 6 A SP MCB C-curve, 2 nos | 300–400 |
| 6 mm laminated sheet + mounting | 100–200 |
| Earth stud, washers, nuts, DIN channel | 100–150 |
| Fixing labour | 150–300 |
| Per pole | ≈ 1,050–1,650 |

# 7. Working logic

## 7.1 Modes

| Mode | Kaise chalta hai |
| --- | --- |
| ASTRO (default) | Panel ki location se roz ka sunrise-sunset khud nikaalta hai. Sunset + 10 min ON, sunrise − 10 min OFF. Offset CMS se badal sakte ho. |
| SCHEDULE | Fixed time (jaise 18:30 ON, 06:00 OFF) aur hafte ke kaun se din. |
| MANUAL | CMS dashboard se turant ON/OFF. MQTT connection hamesha khula, command 1–2 second me lagta hai. |
| Special dates | 8 tareekh tak alag time (Diwali, mela, election). ASTRO aur SCHEDULE ke upar chalta hai. |

Selector switch AUTO pe na ho to controller sirf monitor aur report karta hai. Network chala jaye tab bhi lights panel ke andar ke timer se chalti rehti hain.

## 7.2 Har cycle me kya hota hai

| Step | Kaam |
| --- | --- |
| 1 | Boot: flash se settings, RTC se time. 4G se network time mile to RTC sync. |
| 2 | Har 5 second: meter padho (V, I, kW, PF per phase, total kW, Hz, kWh). |
| 3 | Selector AUTO hai? Nahi to step 6. |
| 4 | Aaj special date hai? Haan to uska time; nahi to mode (ASTRO / SCHEDULE / MANUAL) ke hisaab se ON ya OFF decide karo. |
| 5 | Relay se contactor ON/OFF. |
| 6 | Saare faults check karo (Section 7.3). |
| 7 | Koi fault naya aaya ya clear hua to turant CMS ko event bhejo. |
| 8 | Har 5 minute (CMS se badal sakte ho) poora data bhejo. Network na ho to flash me save, network aate hi bhejo. |
| — | CMS se command aaye to turant apply karo aur jawab bhejo. |

## 7.3 Fault detection

| Fault | Telemetry key | How it is detected | Severity |
| --- | --- | --- | --- |
| Phase fail | f_phaseR/Y/B | Phase voltage below 180 V | Critical |
| Over voltage | f_overVolt | Any phase above 270 V | Major |
| Over current | f_overCurrent | Any phase above the set limit (default 25 A; setLimits for bigger panels) | Major |
| Lamp failure | f_lampR/Y/B | 10 min after switching on, phase power below 95% of the learned baseline (LED drivers are constant-power, so power is steadier than current). Lamps failed ≈ (baseline kW − present kW) / one lamp’s watts. The baseline is learned on the first night or via learnBaseline. With ~83 lamps per phase this catches about 4 or more failed lamps per phase; a single lamp is within meter accuracy. | Major |
| Outgoing MCB trip | f_mcb, mcbTripped (e.g. A-R,B-Y) | Phase voltage present and contactor on, but no 230 V after that MCB | Critical |
| Earth leakage (RCCB trip) | f_earthLeak | Contactor on and phases present, but all 6 MCB outputs dead | Critical |
| Contactor fault | f_contactor | Commanded ON, but no aux feedback or current after 30 s | Critical |
| Day burning | f_dayBurn | Commanded OFF, but current flowing for more than 1 min | Major |
| Door open | f_door | Door limit switch open | Major |
| Meter / supply fail | f_meter | No Modbus reply from the meter. The controller runs on its 18650 cell and still reports. | Critical |
| Network down | — | MQTT disconnected; data buffered in flash | Info |

Limit: panel se ek-ek lamp ki kharabi nahi pakdi ja sakti. 83 lamp per phase pe ek phase me 4 ya zyada lamp band hon tabhi pata chalega. Kaun sa pole kharab hai, ye jaanne ke liye har lamp pe controller lagega, jo spec me nahi hai.

# 8. Firmware aur CMS

## 8.1 Firmware

File: firmware/street_light_panel/street_light_panel.ino (Arduino IDE). Sab 160 panels me ek hi firmware jaata hai. Har panel pehli baar online aate hi CMS me CMS-<IMEI> naam se khud register hota hai aur apna token flash me rakhta hai.

| Setting (file ke upar) | Kya daalna hai |
| --- | --- |
| BOARD_T_A7670 / BOARD_T_SIM7600 | Kaun sa board (default T-A7670) |
| METER_SELEC_MFM383A / METER_SDM630 | Kaun sa meter (default Selec) |
| APN | SIM ka APN (Jio jionet, Airtel airtelgprs.com, Vi www, BSNL bsnlnet, ya M2M SIM ka APN) |
| MQTT_HOST, MQTT_PORT | CMS server ka address, port 1883 |
| PROVISION_KEY, PROVISION_SECRET | CMS me set kiye gaye provisioning key/secret |
| DEFAULT_LAT, DEFAULT_LON | Default location (har panel ki asli location baad me CMS se) |

## 8.2 CMS se commands

| Method | Example params | Effect |
| --- | --- | --- |
| setLight | true | Switch on now (sets MANUAL mode) |
| setMode | "ASTRO" | ASTRO / SCHEDULE / MANUAL |
| setSchedule | {"on":"18:30","off":"06:00","days":127} | days: bit0 = Sunday … bit6 = Saturday (127 = every day) |
| setAstro | {"onOffset":10,"offOffset":-10} | Minutes after sunset / relative to sunrise |
| setSpecial | {"slot":0,"date":"11-08","on":"17:30","off":"06:30"} | Different times on one date (8 slots) |
| learnBaseline | none | Re-learn normal phase currents after lamps are replaced |
| setInterval | 300 | Seconds between normal data uploads (60–3600). Lower data cost with a longer interval. |
| setLimits | {"iMax":25} | Over-current limit per phase (25 A for 10 kW, 35 A for 15 kW, 50 A for 22.5 kW) |
| setLampW | 40 | Wattage of one lamp, for counting failed lamps |
| setLocation | {"lat":28.61,"lon":77.21} | Panel location for sunrise/sunset (set once per panel) |
| getStatus | none | Full live status in the reply |

## 8.3 CMS software: ThingsBoard ya apna

Do raaste hain. Firmware dono ke saath same chalta hai; sirf MQTT_HOST aur provisioning key badalni hai.

|  | ThingsBoard CE (free) | Apna CMS software (PR #2) |
| --- | --- | --- |
| Kya hai | Ready-made open-source IoT platform | Is project ke liye bana Node.js server + web dashboard |
| Shuru karne me time | 1–2 hafte | Phase 1 ready hai (repo me), baaki phases 6–8 hafte |
| Naam / logo | Nahi | Poora aapka |
| License | Free | Free, aapka product |
| Features (abhi) | Dashboard, alarms, history, map | Login + user roles, map, live data, history graph, CSV, alarms, event log, remote control, auto registration |
| Baaki | Scheduled reports paid version me | SMS/email alerts, group scheduling, PDF/Excel reports, Excel import, HTTPS guide |

Apna software Docker se ek server pe chalta hai (cms-server/, docker compose up -d). Server kharcha 160 panel ke liye lagbhag ₹1.5–3.5 lakh, 5 saal. Tender me “hosting / data centre” clause check karna; kai govt tender data India me ya MeitY empanelled cloud pe maangte hain.

Recommendation: tender demo ke liye jo jaldi chal jaaye (dono ready hain), aur lambe samay ke liye apna software, kyunki license zero hai aur product aapka banta hai.

# 9. Panel banane ka tareeka (assembly)

- Enclosure layout: upar incomer + SPD, beech me meter + busbar + contactor + RCCB, neeche outgoing MCBs + terminal blocks. Control compartment (controller, SMPS, modules) alag, power se door. Door pe selector switch aur indicator lamps.

- DIN rails aur wiring duct lagao. Busbar SMC insulators pe, phase colour sleeve ke saath.

- Power wiring (drawing 3): incomer → meter (CT R/Y/B pe, P1 supply side) → busbar → contactor → RCCB → 6 MCB → outgoing terminal blocks. Lugs crimp karo, sab bolt torque se tight.

- SPD: incomer ke baad, chhote aur seedhe wire se earth bar tak (lambi earth wire SPD ko bekar karti hai).

- Control wiring (drawing 4): 6 A MCB → selector → relay RL1 / direct → contactor A1, A2 → N. Aux NO → opto ch7.

- Opto sensing: har outgoing MCB ke neeche wale terminal se opto ch1–6 (A-R, A-Y, A-B, B-R, B-Y, B-B order me), neutral common.

- Low-voltage wiring (drawing 5): SMPS 5 V → LilyGO 5V/GND. RS485 module → meter A/B (twisted pair, end pe 120 Ω). DS3231 aur PCF8574 I2C pe. Relay module, door switch, selector contact. Pull-ups GPIO35/36 pe.

- Earthing: panel body, door (braided strap), SPD, meter, earth bar → 2 earth pits. Har metal part earth se joda ho.

- Labels: har wire pe ferrule number, har MCB pe naam (A-R, B-Y…), panel pe IMEI aur panel number.

- Cable entry: neeche se glands ke through, IP55 bana rahe.

# 10. Testing procedure

Har test ke saamne result likho aur ✓ lagao. Har panel ki ek test sheet file karo (warranty ke liye kaam aayegi).

## 10.1 Bench test (pehla prototype, table pe)

| # | Test | Kaise karein | Expected result | ✓ |
| --- | --- | --- | --- | --- |
| B1 | Firmware compile | Arduino IDE me Verify | Koi error nahi | ☐ |
| B2 | Flash aur boot | USB se upload, Serial Monitor 115200 | Boot message, modem start | ☐ |
| B3 | Meter communication | Meter 230 V pe, RS485 joda | V, I, kW sahi; meter display se ±1% | ☐ |
| B4 | Word order (Selec) | Values galat/bahut bade aayein | WORD_SWAP badal ke dobara | ☐ |
| B5 | 4G + CMS | SIM daalo, power on | Dashboard pe CMS-<IMEI> khud aata hai | ☐ |
| B6 | Location | setLocation bhejo | Sunrise/sunset sahi dikhta hai | ☐ |
| B7 | Remote control | Dashboard switch ON/OFF | Relay 1–2 second me chale | ☐ |
| B8 | Inputs | Door switch, selector, opto (230 V test lamp se) | CMS pe sahi state | ☐ |
| B9 | Offline buffer | SIM nikaalo 15 min, phir lagao | Beech ka data CMS pe aata hai | ☐ |
| B10 | Power fail | 230 V hatao (18650 lagi ho) | Meter fail / supply off alarm CMS pe | ☐ |

## 10.2 Panel test (har panel, factory me, bina load)

| # | Test | Kaise karein | Expected result | ✓ |
| --- | --- | --- | --- | --- |
| P1 | Visual | Wiring drawing se milao, ferrules, torque | Sab sahi aur tight | ☐ |
| P2 | Continuity | Multimeter se har power aur control wire | Har circuit sahi jagah | ☐ |
| P3 | Insulation | 500 V megger: phase-phase, phase-N, phase-earth (controller aur SMPS hata ke) | ≥ 1 MΩ (aam taur pe kaafi zyada) | ☐ |
| P4 | Earth continuity | Body, door, SPD, earth bar ke beech | ≈ 0 Ω (< 0.5 Ω) | ☐ |
| P5 | Phase sequence | Supply dene ke baad phase sequence meter | R-Y-B sahi, meter pe teeno V aayein | ☐ |
| P6 | Selector MANUAL | Selector MAN | Contactor turant ON | ☐ |
| P7 | Selector AUTO | AUTO + CMS se ON/OFF | Contactor command pe chale, aux feedback CMS pe | ☐ |
| P8 | RCCB | Test button dabao; RCD tester se 300 mA | Trip ho; CMS pe earth leakage alarm | ☐ |
| P9 | MCB sense | Har outgoing MCB ek-ek karke band | CMS pe sahi naam (A-R … B-B) | ☐ |
| P10 | Door | Door kholo | Door alarm | ☐ |
| P11 | Soak test | 24 ghante chalao | Koi reboot nahi, data har 5 min | ☐ |

## 10.3 Load test (prototype ya sample panel)

| # | Test | Kaise karein | Expected result | ✓ |
| --- | --- | --- | --- | --- |
| L1 | Load ON | Asli feeder ya test load se ON | kW, PF sahi; teeno phase balance | ☐ |
| L2 | Baseline | 10 min baad (ya learnBaseline) | Base power save | ☐ |
| L3 | Lamp failure | Ek phase pe 4–5 lamp band | Lamp failure alarm, approx lamp count | ☐ |
| L4 | Over current | setLimits me iMax kam karke | Over current alarm | ☐ |
| L5 | Day burning | AUTO me OFF time pe MANUAL kar do | 1 min baad day burning alarm | ☐ |
| L6 | Contactor fault | Coil ka wire nikaal ke ON command | 30 s baad contactor fault | ☐ |
| L7 | ASTRO | 1–2 hafte chalao | Roz sahi time pe ON/OFF, event log me record | ☐ |

## 10.4 Site commissioning (har panel)

| # | Kaam | Expected result | ✓ |
| --- | --- | --- | --- |
| S1 | Plinth / foundation, panel level aur fix | Mazboot, paani na ghuse | ☐ |
| S2 | 2 earth pits, earth resistance test | Kam se kam (aam taur pe < 5 Ω, ya tender ke hisaab se) | ☐ |
| S3 | Incoming aur feeder cable termination, glands | Tight, IP55 bana rahe | ☐ |
| S4 | Feeder insulation test (lamps hata ke ya MCB off) | ≥ 1 MΩ | ☐ |
| S5 | Lamps R-Y-B baari baari jude hain | Teeno phase ka kW lagbhag barabar | ☐ |
| S6 | Power on, CMS pe panel online | CMS-<IMEI> online, signal (rssi) theek | ☐ |
| S7 | Location aur naam set | Map pe sahi jagah, ward/road naam | ☐ |
| S8 | Remote ON/OFF, MANUAL selector | Dono kaam karein | ☐ |
| S9 | Voltage drop | Feeder ke last pole pe voltage | Supply se ~5% se kam gira |
| S10 | Handover | Test sheet, IMEI, photos file | Record complete |

# 11. Bid estimate (160 panels + CMS, 5 saal)

| Item | Per panel ₹ | 160 panels ₹ |
| --- | --- | --- |
| Panel material (10 kW tender build, ~10% bulk discount) | 23,000–29,500 | 36.8–47.2 lakh |
| Assembly, wiring, testing per panel | 2,500–3,500 | 4.0–5.6 lakh |
| Transport | 500–1,000 | 0.8–1.6 lakh |
| Site installation and commissioning (plinth, 2 earth pits, terminations) | 8,000–12,000 | 12.8–19.2 lakh |
| SIM data, 5 years (M2M plan) | 2,400–6,000 | 3.8–9.6 lakh |
| CMS server 5 years + dashboard setup | — | 2.5–4.0 lakh |
| Spares and warranty visits reserve (~10% of panel material) | 2,300–2,950 | 3.7–4.7 lakh |
| Prototype and development (one-time) | — | 1.0–2.0 lakh |
| Total before profit and GST |  | ≈ ₹65–94 lakh |

Iske upar apna margin aur 18% GST. 60 W ya 90 W lamp ho to rating table ka extra cost jodo (160 panel pe ₹4.8–9.6 lakh). Feeder cable aur poles isme nahi hain. Spec ka per-pole saamaan agar sab 40,000 pole pe lagna hai to ≈ ₹4.2–6.6 crore alag.

# 12. Safety

415 V jaan le sakta hai. Power wiring aur testing licensed electrician se karwao. Panel body aur door earth karo. Panel ke andar kaam se pehle incomer OFF karke lock karo (lock-out). Megger test se pehle controller, SMPS aur opto module ke wire hata do.

# 13. Abhi kya tay karna baaki hai

- Har pole pe lamp kitne watt ka hai (panel rating isi se tay hogi).

- Naye pole kitne hain, aur window box ka saamaan sab 40,000 pole pe lagna hai ya sirf naye pe.

- CMS: ThingsBoard ya apna software, aur server kahan host hoga (tender ka hosting clause).

- Firmware ka pehla compile aur bench test (Section 10.1); Selec meter ka word order confirm.

# Appendix A. Firmware code

/*
  Smart Feeder Control Panel (Street Light) -> CMS dashboard
  ----------------------------------------------------------
  Board  : LilyGO T-A7670E (ESP32 + 4G LTE Cat-1, sasta)  [ya T-SIM7600E]
  Meter  : Selec MFM383A-C (3-phase, RS485, slave id 1, 9600 8N1)  [ya Eastron SDM630]
  RTC    : DS3231 (I2C)
  CMS    : ThingsBoard (MQTT, device access token)

  Libraries (Arduino Library Manager se install karo):
    TinyGSM, PubSubClient, ModbusMaster, RTClib, ArduinoJson (v7)
    (T-A7670 ke liye agar TinyGSM me A7670 na mile to LilyGO-T-A76XX repo
     ke "lib" folder wali TinyGSM use karo)
  Board package: "esp32 by Espressif", board = "ESP32 Dev Module",
    Partition scheme = "Default 4MB with spiffs" (LittleFS ke liye)

  NOTE: Pin numbers LilyGO T-A7670 / T-SIM7600 ke hisaab se hain. Apne board ka
        pinout zaroor check karo. GPIO 34-39 input-only hain, inpe
        10k external pull-up lagana hai.
*/

// ---- Hardware choice: ek board aur ek meter chuno ----
#define BOARD_T_A7670        // sasta (tender default). Mehenga option: BOARD_T_SIM7600
#define METER_SELEC_MFM383A  // sasta (tender default). Mehenga option: METER_SDM630

#if defined(BOARD_T_A7670)
  #define TINY_GSM_MODEM_A7670
#else
  #define TINY_GSM_MODEM_SIM7600
#endif
#define TINY_GSM_RX_BUFFER 1024
#include <TinyGsmClient.h>
#include <PubSubClient.h>
#include <ModbusMaster.h>
#include <RTClib.h>
#include <ArduinoJson.h>
#include <Preferences.h>
#include <LittleFS.h>
#include <math.h>

// ================== SETTINGS (apne hisaab se badlo) ==================
const char APN[]          = "airtelgprs.com";   // Jio: "jionet", Vi: "www", BSNL: "bsnlnet"
const char MQTT_HOST[]    = "cms.example.com";  // aapka ThingsBoard server
const uint16_t MQTT_PORT  = 1883;
// 160 panels me SAME firmware jaata hai. Har panel pehli baar online aate hi
// ThingsBoard "device provisioning" se apna token khud le leta hai (naam = CMS-<IMEI>).
// Location CMS se setLocation command se set hoti hai (ya neeche default).
const char PROVISION_KEY[]    = "cms-provision-key";     // ThingsBoard device profile me set karo
const char PROVISION_SECRET[] = "cms-provision-secret";
const float DEFAULT_LAT = 28.61, DEFAULT_LON = 77.21;    // jab tak setLocation na aaye (example: Delhi)
const float TZ_HOURS = 5.5;                     // IST

// Fault limits
const float V_LOW = 180, V_HIGH = 270;          // volts (phase-neutral)
// LED driver constant-power hote hain, isliye lamp failure POWER (kW) se check hota hai,
// current se nahi. ~83 lamp/phase pe 5% drop = ~4 lamp band. Isse chhota farq meter
// accuracy (class 1) me chhup jaata hai.
const float LAMP_DROP = 0.95;
const uint32_t SETTLE_MS = 10UL * 60 * 1000;    // ON hone ke 10 min baad hi lamp check

// ================== PINS (LilyGO T-A7670 / T-SIM7600) ==================
#define MODEM_TX      27
#define MODEM_RX      26
#define MODEM_PWRKEY  4
#if defined(BOARD_T_A7670)
  #define MODEM_POWERON 12   // board ka modem power enable
#else
  #define MODEM_FLIGHT  25
#endif
#define RS485_RX      18   // TTL-RS485 module (auto direction) ka TXD
#define RS485_TX      19   // TTL-RS485 module ka RXD
#define I2C_SDA       21   // DS3231
#define I2C_SCL       22
#define PIN_RELAY     23   // relay -> contactor coil (AUTO path)
#define PIN_DOOR      35   // door limit switch, LOW = door band
#define PIN_AUX       36   // contactor aux NO via 230V opto, LOW = contactor ON
// 6 outgoing MCB (Feeder A: R,Y,B  Feeder B: R,Y,B) ke baad 230V opto -> PCF8574
// I2C expander (RTC wali I2C line pe). Bit 0-5 = A-R, A-Y, A-B, B-R, B-Y, B-B.
// Bit LOW = MCB ke baad supply hai.
#define PCF8574_ADDR  0x20
#define PIN_SEL_AUTO  15   // selector switch AUTO position, LOW = AUTO
#define RELAY_ON_LEVEL HIGH

// ================== OBJECTS ==================
HardwareSerial SerialAT(1);
TinyGsm modem(SerialAT);
TinyGsmClient gsmClient(modem);
PubSubClient mqtt(gsmClient);
ModbusMaster meterBus;
RTC_DS3231 rtc;
Preferences prefs;

// ================== DATA ==================
struct Meter {
  float v[3], i[3], p[3], pf[3];
  float kwTotal, freq, kwh;
  bool ok;
} m;

struct Special { uint16_t mmdd; int16_t onMin, offMin; };  // mmdd=0 means empty

enum Mode : uint8_t { MODE_ASTRO = 0, MODE_SCHEDULE = 1, MODE_MANUAL = 2 };

struct Config {
  uint8_t mode;
  int16_t onOffset, offOffset;   // ASTRO: sunset+onOffset ON, sunrise+offOffset OFF (minutes)
  int16_t onMin, offMin;         // SCHEDULE: minutes from midnight
  uint8_t dayMask;               // bit0=Sun ... bit6=Sat
  bool manualState;
  float basePw[3];               // normal power per phase (kW), auto-learn
  float lampW;                   // ek lamp ki wattage (W), e.g. 40
  float lat, lon;                // panel location (ASTRO ke liye)
  float iMax;                    // over-current limit per phase (A): 10kW=25, 15kW=35, 22kW=50
  char token[40];                // ThingsBoard access token (provisioning se aata hai)
  uint16_t publishSec;           // normal data kitne second me bheje (data/SIM kharcha kam)
  Special specials[8];           // date-wise override (festival etc.)
} cfg;

enum Fault : uint32_t {
  F_PHASE_R = 1UL << 0, F_PHASE_Y = 1UL << 1, F_PHASE_B = 1UL << 2,
  F_OVERVOLT = 1UL << 3, F_OVERCURRENT = 1UL << 4,
  F_LAMP_R = 1UL << 5, F_LAMP_Y = 1UL << 6, F_LAMP_B = 1UL << 7,
  F_CONTACTOR = 1UL << 8, F_DAY_BURN = 1UL << 9,
  F_MCB = 1UL << 10, F_EARTH_LEAK = 1UL << 11,
  F_DOOR = 1UL << 12, F_METER = 1UL << 13
};
const char* FAULT_KEYS[] = {
  "f_phaseR", "f_phaseY", "f_phaseB", "f_overVolt", "f_overCurrent",
  "f_lampR", "f_lampY", "f_lampB", "f_contactor", "f_dayBurn",
  "f_mcb", "f_earthLeak", "f_door", "f_meter"
};
const int FAULT_COUNT = sizeof(FAULT_KEYS) / sizeof(FAULT_KEYS[0]);

uint32_t faults = 0, lastFaults = 0;
bool lightOn = false;
uint32_t onSinceMs = 0, dayBurnSinceMs = 0;
int sunriseMin = 360, sunsetMin = 1080;
int failedLamps[3] = {0, 0, 0};
String mcbTripped = "";   // jaise "A-R,B-Y"
uint32_t tRead = 0, tPublish = 0, tConnect = 0;

// ================== TIME HELPERS ==================
DateTime localNow() { return rtc.now() + TimeSpan((int32_t)(TZ_HOURS * 3600)); }
uint64_t epochMs() { return (uint64_t)rtc.now().unixtime() * 1000ULL; }

int dayOfYear(const DateTime& d) {
  static const int cum[] = {0, 31, 59, 90, 120, 151, 181, 212, 243, 273, 304, 334};
  int n = cum[d.month() - 1] + d.day();
  bool leap = (d.year() % 4 == 0 && d.year() % 100 != 0) || d.year() % 400 == 0;
  return (leap && d.month() > 2) ? n + 1 : n;
}

// Sunrise/sunset (NOAA "Almanac" method). Returns local minutes from midnight, -1 if none.
int sunEvent(int doy, bool rising) {
  const float RAD = M_PI / 180.0, ZENITH = 90.833;
  float lngHour = cfg.lon / 15.0;
  float t = doy + ((rising ? 6 : 18) - lngHour) / 24.0;
  float M = 0.9856 * t - 3.289;
  float L = fmod(M + 1.916 * sin(M * RAD) + 0.020 * sin(2 * M * RAD) + 282.634 + 360, 360);
  float RA = fmod(atan(0.91764 * tan(L * RAD)) / RAD + 360, 360);
  RA += floor(L / 90) * 90 - floor(RA / 90) * 90;
  RA /= 15;
  float sinDec = 0.39782 * sin(L * RAD);
  float cosDec = cos(asin(sinDec));
  float cosH = (cos(ZENITH * RAD) - sinDec * sin(cfg.lat * RAD)) / (cosDec * cos(cfg.lat * RAD));
  if (cosH > 1 || cosH < -1) return -1;
  float H = (rising ? 360 - acos(cosH) / RAD : acos(cosH) / RAD) / 15;
  float T = H + RA - 0.06571 * t - 6.622;
  float local = fmod(T - lngHour + TZ_HOURS + 48, 24);
  return (int)(local * 60);
}

// ON window jo midnight cross kar sakti hai (e.g. 18:30 -> 06:00)
bool inWindow(int now, int on, int off) {
  return (on <= off) ? (now >= on && now < off) : (now >= on || now < off);
}

int parseHHMM(const char* s) { int h = 0, mi = 0; sscanf(s, "%d:%d", &h, &mi); return h * 60 + mi; }

// ================== CONFIG ==================
void loadConfig() {
  prefs.begin("panel", false);
  if (prefs.getBytes("cfg", &cfg, sizeof(cfg)) != sizeof(cfg)) {
    memset(&cfg, 0, sizeof(cfg));
    cfg.mode = MODE_ASTRO;
    cfg.onOffset = 10;   // sunset ke 10 min baad ON
    cfg.offOffset = -10; // sunrise se 10 min pehle OFF
    cfg.onMin = 18 * 60 + 30;
    cfg.offMin = 6 * 60;
    cfg.dayMask = 0x7F;
    cfg.lampW = 40;
    cfg.lat = DEFAULT_LAT; cfg.lon = DEFAULT_LON;
    cfg.iMax = 25;
    cfg.publishSec = 300;  // 5 min. Faults/events phir bhi turant jaate hain
  }
}
void saveConfig() { prefs.putBytes("cfg", &cfg, sizeof(cfg)); }

// ================== METER (Modbus RS485) ==================
// Register map (input registers, function 04, float = 2 registers).
// Selec ka map aggsoft.com ki list se hai; word order meter ke manual ya
// "Modbus Poll" software se ek baar check kar lo (galat ho to WORD_SWAP badlo).
#if defined(METER_SDM630)
  const uint16_t R_V[3] = {0, 2, 4}, R_I[3] = {6, 8, 10}, R_P[3] = {12, 14, 16}, R_PF[3] = {30, 32, 34};
  const uint16_t R_KW = 52, R_FREQ = 70, R_KWH = 72;
  const float P_DIV = 1000.0;   // SDM630 power W me deta hai
  const bool WORD_SWAP = false; // high word pehle
#else  // Selec MFM383A-C
  const uint16_t R_V[3] = {0, 2, 4}, R_I[3] = {16, 18, 20}, R_P[3] = {24, 26, 28}, R_PF[3] = {48, 50, 52};
  const uint16_t R_KW = 42, R_FREQ = 56, R_KWH = 58;
  const float P_DIV = 1.0;      // kW me
  const bool WORD_SWAP = true;  // low word pehle (verify karo)
#endif

bool readFloat(uint16_t reg, float& out) {
  if (meterBus.readInputRegisters(reg, 2) != meterBus.ku8MBSuccess) return false;
  uint16_t a = meterBus.getResponseBuffer(0), b = meterBus.getResponseBuffer(1);
  uint32_t raw = WORD_SWAP ? ((uint32_t)b << 16) | a : ((uint32_t)a << 16) | b;
  memcpy(&out, &raw, 4);
  return true;
}

void readMeter() {
  bool ok = true;
  for (int k = 0; k < 3; k++) {
    ok &= readFloat(R_V[k], m.v[k]);
    ok &= readFloat(R_I[k], m.i[k]);
    ok &= readFloat(R_P[k], m.p[k]);  m.p[k] /= P_DIV;
    ok &= readFloat(R_PF[k], m.pf[k]);
  }
  ok &= readFloat(R_KW, m.kwTotal);  m.kwTotal /= P_DIV;
  ok &= readFloat(R_FREQ, m.freq);
  ok &= readFloat(R_KWH, m.kwh);
  m.ok = ok;
}

// ================== LIGHT DECISION ==================
bool selectorAuto() { return digitalRead(PIN_SEL_AUTO) == LOW; }

void setLight(bool on) {
  if (on && !lightOn) onSinceMs = millis();
  lightOn = on;
  digitalWrite(PIN_RELAY, on ? RELAY_ON_LEVEL : !RELAY_ON_LEVEL);
}

void decideLight() {
  DateTime d = localNow();
  int nowMin = d.hour() * 60 + d.minute();
  int doy = dayOfYear(d);
  sunriseMin = sunEvent(doy, true);
  sunsetMin = sunEvent(doy, false);

  bool want = false;
  uint16_t mmdd = d.month() * 100 + d.day();
  const Special* sp = nullptr;
  for (auto& s : cfg.specials) if (s.mmdd == mmdd) sp = &s;

  if (cfg.mode == MODE_MANUAL) {
    want = cfg.manualState;
  } else if (sp) {
    want = inWindow(nowMin, sp->onMin, sp->offMin);
  } else if (cfg.mode == MODE_ASTRO) {
    want = inWindow(nowMin, sunsetMin + cfg.onOffset, sunriseMin + cfg.offOffset);
  } else {  // SCHEDULE
    // subah ka hissa (midnight ke baad) pichle din ki schedule maana jaata hai
    int dow = d.dayOfTheWeek();
    if (cfg.onMin > cfg.offMin && nowMin < cfg.offMin) dow = (dow + 6) % 7;
    want = (cfg.dayMask & (1 << dow)) && inWindow(nowMin, cfg.onMin, cfg.offMin);
  }
  setLight(want);
}

// ================== FAULT DETECTION ==================
uint8_t readExpander() {
  if (Wire.requestFrom(PCF8574_ADDR, 1) != 1) return 0x00;  // expander na mile to "sab theek" maano
  return Wire.read();
}

void checkFaults() {
  uint32_t f = 0;
  const uint32_t phaseBits[3] = {F_PHASE_R, F_PHASE_Y, F_PHASE_B};
  const uint32_t lampBits[3]  = {F_LAMP_R, F_LAMP_Y, F_LAMP_B};
  static const char* MCB_NAMES[6] = {"A-R", "A-Y", "A-B", "B-R", "B-Y", "B-B"};

  if (digitalRead(PIN_DOOR) == HIGH) f |= F_DOOR;
  if (!m.ok) { f |= F_METER; faults = f; return; }

  bool contactorOn = digitalRead(PIN_AUX) == LOW;
  bool settled = lightOn && (millis() - onSinceMs > SETTLE_MS);
  float totalI = 0;

  for (int k = 0; k < 3; k++) {
    totalI += m.i[k];
    if (m.v[k] < V_LOW) f |= phaseBits[k];
    if (m.v[k] > V_HIGH) f |= F_OVERVOLT;
    if (m.i[k] > cfg.iMax) f |= F_OVERCURRENT;
    bool phaseOk = m.v[k] >= V_LOW;


    // Lamp failure: phase ki power normal (base) se 5% se zyada kam
    failedLamps[k] = 0;
    if (settled && phaseOk && cfg.basePw[k] > 0.1 && m.p[k] < cfg.basePw[k] * LAMP_DROP) {
      f |= lampBits[k];
      failedLamps[k] = (int)roundf((cfg.basePw[k] - m.p[k]) * 1000.0 / cfg.lampW);
    }
  }

  // Outgoing MCB / RCCB trip: phase hai, contactor ON hai, par MCB ke baad supply nahi
  mcbTripped = "";
  if (contactorOn) {
    uint8_t in = readExpander();
    int dead = 0, live = 0;
    for (int j = 0; j < 6; j++) {
      if (m.v[j % 3] < V_LOW) continue;          // phase hi nahi hai, wo phase fault hai
      live++;
      if (in & (1 << j)) {                        // HIGH = supply nahi
        dead++;
        if (mcbTripped.length()) mcbTripped += ",";
        mcbTripped += MCB_NAMES[j];
      }
    }
    if (live > 0 && dead == live) f |= F_EARTH_LEAK;  // sab feeder band = RCCB trip
    else if (dead > 0) f |= F_MCB;
  }

  // Pehli baar: base power khud seekh lo
  if (settled && cfg.basePw[0] == 0 && cfg.basePw[1] == 0 && cfg.basePw[2] == 0 && totalI > 1.0) {
    for (int k = 0; k < 3; k++) cfg.basePw[k] = m.p[k];
    saveConfig();
  }

  // Contactor fault: command ON tha par contactor/current nahi aaya
  if (selectorAuto() && lightOn && millis() - onSinceMs > 30000 && (!contactorOn || totalI < 0.3))
    f |= F_CONTACTOR;

  // Day burning: command OFF hai par lights jal rahi hain (1 min se zyada)
  if (selectorAuto() && !lightOn && totalI > 0.5) {
    if (!dayBurnSinceMs) dayBurnSinceMs = millis();
    if (millis() - dayBurnSinceMs > 60000) f |= F_DAY_BURN;
  } else dayBurnSinceMs = 0;

  faults = f;
}

// ================== TELEMETRY + OFFLINE LOG ==================
void buildTelemetry(JsonObject v) {
  const char* ph[3] = {"R", "Y", "B"};
  for (int k = 0; k < 3; k++) {
    v[String("v") + ph[k]]  = m.v[k];
    v[String("i") + ph[k]]  = m.i[k];
    v[String("kw") + ph[k]] = m.p[k];
    v[String("pf") + ph[k]] = m.pf[k];
    v[String("lampsFailed") + ph[k]] = failedLamps[k];
  }
  v["kwTotal"] = m.kwTotal; v["freq"] = m.freq; v["kwh"] = m.kwh;
  v["light"] = lightOn;
  v["mode"] = cfg.mode == MODE_ASTRO ? "ASTRO" : cfg.mode == MODE_SCHEDULE ? "SCHEDULE" : "MANUAL";
  v["selector"] = selectorAuto() ? "AUTO" : "LOCAL";
  v["sunrise"] = sunriseMin; v["sunset"] = sunsetMin;
  v["rssi"] = modem.getSignalQuality();
  for (int b = 0; b < FAULT_COUNT; b++) v[FAULT_KEYS[b]] = (bool)(faults & (1UL << b));
  v["mcbTripped"] = mcbTripped;
}

void logOffline(const String& line) {
  File fl = LittleFS.open("/queue.jsonl", FILE_APPEND);
  if (fl && fl.size() < 900000) fl.println(line);   // ~1MB tak store
  if (fl) fl.close();
}

void flushOffline() {
  if (!LittleFS.exists("/queue.jsonl")) return;
  File fl = LittleFS.open("/queue.jsonl", FILE_READ);
  while (fl.available() && mqtt.connected()) {
    String line = fl.readStringUntil('\n');
    line.trim();
    if (line.length()) mqtt.publish("v1/devices/me/telemetry", line.c_str());
    mqtt.loop();
  }
  fl.close();
  LittleFS.remove("/queue.jsonl");
}

void publishTelemetry() {
  JsonDocument doc;
  doc["ts"] = epochMs();
  buildTelemetry(doc["values"].to<JsonObject>());
  String out; serializeJson(doc, out);
  if (mqtt.connected()) mqtt.publish("v1/devices/me/telemetry", out.c_str());
  else logOffline(out);
}

// Event log: har fault RAISED / CLEARED turant bhejo
void publishEvents() {
  uint32_t changed = faults ^ lastFaults;
  if (!changed) return;
  for (int b = 0; b < FAULT_COUNT; b++) {
    if (!(changed & (1UL << b))) continue;
    JsonDocument doc;
    doc["ts"] = epochMs();
    doc["values"]["event"] = String(FAULT_KEYS[b]) + ((faults & (1UL << b)) ? " RAISED" : " CLEARED");
    String out; serializeJson(doc, out);
    if (mqtt.connected()) mqtt.publish("v1/devices/me/telemetry", out.c_str());
    else logOffline(out);
  }
  lastFaults = faults;
  publishTelemetry();  // alarm ke saath latest values bhi
}

// ================== COMMANDS FROM CMS (RPC) ==================
bool provisioned = false;

void onMqtt(char* topic, byte* payload, unsigned int len) {
  String t(topic);
  if (t == "/provision/response") {           // {"status":"SUCCESS","credentialsValue":"..."}
    JsonDocument r;
    if (!deserializeJson(r, payload, len) && String(r["status"] | "") == "SUCCESS") {
      strlcpy(cfg.token, r["credentialsValue"] | "", sizeof(cfg.token));
      saveConfig();
      provisioned = true;
    }
    return;
  }
  String reqId = t.substring(t.lastIndexOf('/') + 1);
  JsonDocument req;
  if (deserializeJson(req, payload, len)) return;
  String method = req["method"] | "";
  JsonVariant p = req["params"];
  JsonDocument res; res["ok"] = true;

  if (method == "setLight") {                 // {"method":"setLight","params":true}
    cfg.mode = MODE_MANUAL; cfg.manualState = p.as<bool>();
  } else if (method == "setMode") {           // "ASTRO" | "SCHEDULE" | "MANUAL"
    String md = p.as<String>();
    cfg.mode = md == "SCHEDULE" ? MODE_SCHEDULE : md == "MANUAL" ? MODE_MANUAL : MODE_ASTRO;
  } else if (method == "setSchedule") {       // {"on":"18:30","off":"06:00","days":127}
    cfg.onMin = parseHHMM(p["on"] | "18:30");
    cfg.offMin = parseHHMM(p["off"] | "06:00");
    cfg.dayMask = p["days"] | 0x7F;
  } else if (method == "setAstro") {          // {"onOffset":10,"offOffset":-10}
    cfg.onOffset = p["onOffset"] | 0; cfg.offOffset = p["offOffset"] | 0;
  } else if (method == "setSpecial") {        // {"slot":0,"date":"10-31","on":"17:30","off":"06:30"}
    int slot = p["slot"] | 0;
    int mo = 0, dy = 0; sscanf(p["date"] | "00-00", "%d-%d", &mo, &dy);
    if (slot >= 0 && slot < 8) cfg.specials[slot] = {(uint16_t)(mo * 100 + dy),
      (int16_t)parseHHMM(p["on"] | "00:00"), (int16_t)parseHHMM(p["off"] | "00:00")};
  } else if (method == "learnBaseline") {     // naye lamps lagne ke baad
    for (int k = 0; k < 3; k++) cfg.basePw[k] = m.p[k];
  } else if (method == "setInterval") {     // seconds, 60..3600
    cfg.publishSec = constrain(p.as<int>(), 60, 3600);
  } else if (method == "setLimits") {        // {"iMax":25}
    cfg.iMax = p["iMax"] | cfg.iMax;
  } else if (method == "setLampW") {         // 40
    cfg.lampW = p.as<float>();
  } else if (method == "setLocation") {      // {"lat":28.61,"lon":77.21}
    cfg.lat = p["lat"] | cfg.lat; cfg.lon = p["lon"] | cfg.lon;
  } else if (method == "getStatus") {
    buildTelemetry(res["status"].to<JsonObject>());
  } else {
    res["ok"] = false; res["error"] = "unknown method";
  }
  saveConfig();
  decideLight();   // command turant apply, koi delay nahi

  String out; serializeJson(res, out);
  mqtt.publish(("v1/devices/me/rpc/response/" + reqId).c_str(), out.c_str());
  publishTelemetry();
}

// ================== NETWORK ==================
void syncTimeFromNetwork() {
  int y, mo, d, h, mi, s; float tz;
  if (modem.getNetworkTime(&y, &mo, &d, &h, &mi, &s, &tz) && y >= 2025) {
    DateTime localT(y, mo, d, h, mi, s);
    rtc.adjust(localT - TimeSpan((int32_t)(tz * 3600)));  // RTC me UTC rakhte hain
  }
}

void ensureConnected() {
  if (mqtt.connected()) return;
  if (millis() - tConnect < 30000 && tConnect) return;  // har 30 s retry
  tConnect = millis();
  if (!modem.isNetworkConnected() && !modem.waitForNetwork(20000)) return;
  if (!modem.isGprsConnected() && !modem.gprsConnect(APN)) return;
  syncTimeFromNetwork();
  mqtt.setServer(MQTT_HOST, MQTT_PORT);
  mqtt.setCallback(onMqtt);
  mqtt.setKeepAlive(30);
  mqtt.setBufferSize(1024);
  String imei = modem.getIMEI();
  String clientId = "CMS-" + imei;          // har panel ka alag client id

  // Pehli baar: ThingsBoard se apna token lo
  if (cfg.token[0] == 0) {
    if (!mqtt.connect(clientId.c_str(), "provision", nullptr)) return;
    mqtt.subscribe("/provision/response");
    JsonDocument req;
    req["deviceName"] = clientId;
    req["provisionDeviceKey"] = PROVISION_KEY;
    req["provisionDeviceSecret"] = PROVISION_SECRET;
    String out; serializeJson(req, out);
    provisioned = false;
    mqtt.publish("/provision/request", out.c_str());
    for (uint32_t t0 = millis(); !provisioned && millis() - t0 < 15000;) mqtt.loop();
    mqtt.disconnect();
    if (!provisioned) return;               // 30 s baad phir try
  }

  if (mqtt.connect(clientId.c_str(), cfg.token, nullptr)) {
    mqtt.subscribe("v1/devices/me/rpc/request/+", 1);
    flushOffline();
    publishTelemetry();
  } else if (mqtt.state() == MQTT_CONNECT_UNAUTHORIZED) {
    cfg.token[0] = 0;  // CMS pe device delete hua: agli baar dobara provision
    saveConfig();
  }
}

// ================== SETUP / LOOP ==================
void setup() {
  Serial.begin(115200);
  pinMode(PIN_RELAY, OUTPUT); digitalWrite(PIN_RELAY, !RELAY_ON_LEVEL);
  pinMode(PIN_DOOR, INPUT); pinMode(PIN_AUX, INPUT);  // external pull-up
  pinMode(PIN_SEL_AUTO, INPUT_PULLUP);

  Wire.begin(I2C_SDA, I2C_SCL);
  Wire.beginTransmission(PCF8574_ADDR); Wire.write(0xFF); Wire.endTransmission();  // sab pins input
  rtc.begin();
  LittleFS.begin(true);
  loadConfig();

  Serial2.begin(9600, SERIAL_8N1, RS485_RX, RS485_TX);
  meterBus.begin(1, Serial2);

  // 4G modem power on
#if defined(BOARD_T_A7670)
  pinMode(MODEM_POWERON, OUTPUT); digitalWrite(MODEM_POWERON, HIGH);
  pinMode(MODEM_PWRKEY, OUTPUT);
  digitalWrite(MODEM_PWRKEY, LOW); delay(100); digitalWrite(MODEM_PWRKEY, HIGH); delay(100); digitalWrite(MODEM_PWRKEY, LOW);
#else
  pinMode(MODEM_PWRKEY, OUTPUT);
  digitalWrite(MODEM_PWRKEY, HIGH); delay(300); digitalWrite(MODEM_PWRKEY, LOW);
  pinMode(MODEM_FLIGHT, OUTPUT); digitalWrite(MODEM_FLIGHT, HIGH);
#endif
  SerialAT.begin(115200, SERIAL_8N1, MODEM_RX, MODEM_TX);
  delay(3000);
  modem.restart();

  readMeter(); decideLight(); checkFaults();  // network na ho tab bhi lights chalti rahein
}

void loop() {
  mqtt.loop();                                  // commands turant receive
  if (millis() - tRead > 5000) {                // har 5 s
    tRead = millis();
    readMeter(); decideLight(); checkFaults(); publishEvents();
  }
  if (millis() - tPublish > cfg.publishSec * 1000UL) {  // default har 5 min data log
    tPublish = millis();
    publishTelemetry();
  }
  ensureConnected();
}